Product: Double Duty™ - 12 Trap and Pump Combination

Category: Trap and Pump Combination

Type: Double Duty

Model: DD12

Part 1	General

  - Summary

  - Submittals

  - Delivery, storage and handling

  - Warranty

Part 2	Products

  - Pressure Driven Steam Trap and Pump Combination

Part 3	Execution

3.01 Installation

Part 1 – General

  - Summary

- Selection Includes

  - Pressure Driven Steam Trap and Pump Combination

  - Submittals

- Submit the following in accordance with this specification:

  - Tag number as referred to on drawing

  - Manufacturer’s name and model number

  - Capacity and Maximum Pressure Ratings

  - Materials of construction

  - Dimensions and weights

  - All other essential data as identified in Owner’s specifications.

  - Delivery, Storage and Handling

- Receipt. Contractor or end user shall receive and store Pump Traps in a manner that will protect them from weather and construction activity.

- Examination. Upon receipt, contractor or end user shall visually inspect all condensate Pump Traps for damage and compare each pump to their corresponding specification.

  - Warranty. Guarantee that the equipment will be free from defects in materials and workmanship for a period of 12 months from date of installation but in no event longer than 15 months after shipment from Armstrong’s factory.

Part 2 – Products

  - Pressure Driven Steam Trap and Pump Combination

- Acceptable Manufacturers

  - Armstrong Intl, Inc. Model DD-12

- Body shall be an ASME code Sec. VIII U stamped carbon steel vessel rated to 200 psig @ 400°F with all stainless steel internals. The vessel shall have a 6-3/4” inspection port which allows access to the internal trap mechanism.

- The pump mechanism shall incorporate Inconel X-750 springs for superior service life. Springs made of materials other than Inconel X-750 shall not be accepted. Single compression springs shall not be accepted. Motive and vent connections shall have externally replaceable seats for viewing and inspecting the internal valves.

- Internal pump and steam trap mechanisms shall not be integrally linked. The steam trap mechanism should be accessible without disturbing the motive and vent piping.

- Check valves shall be external for easy access.

- Motive Force. The Pump Trap shall utilize steam to remove condensate from the receiving vessel.

- Trap/Pump shall require no electricity for operation.

- The DD-12 shall include a bronze water level gauge with shut off valves.

- Overall height of the trap/pump shall not exceed 28”.

- The pump shall have 150# RF flanges for condensate inlet and outlet. Optional 300# flanges available.

- Check valves shall be WLC wafer style constructed of carbon steel with stainless steel trim.

- Provide Trap/Pump with pressure gauge assembly.

- Manufacturer’s standard painting will apply.

Part 3 – Execution:

  - Installation

- Installation Compliance. Install in accordance with manufacturer’s instructions and as shown on the drawing.

- Insulation. Install the removable insulation cover in accordance with manufacturer’s instructions.

End of Section