DPT-308 Low Boy™ Pump Trap Receiver Package

Category: Pump Trap

Type: Receiver Package

Model: DPT-308 Low Boy™

Part 1 – General

  - Summary

- Selection Includes

  - Pressure Driven Condensate Pump Trap Receiver Package

  - Submittals

- Submit the following in accordance with this specification:

  - Tag number as referred to on drawing

  - Manufacturer’s name and model number

  - Capacity and Maximum Pressure Ratings

  - Materials of construction

  - Dimensions and weights

  - All other essential data as identified in Owner’s specifications.

  - Delivery, Storage and Handling

- Receipt. Contractor or end user shall receive and store Pump Traps in a manner that will protect them from weather and construction activity.

- Examination. Upon receipt, contractor or end user shall visually inspect all condensate Pump Traps for damage and compare each pump to their corresponding specification.

  - Warranty. Product shall be free from defects in material and workmanship for a period of one (1) year from date of installation, but not longer than 15 months from date of shipment from the factory.  This warranty does not extend to any product that has been subject to misuse, neglect, or alteration after shipment from Armstrong factory.

Part 2 – Products

  - Pressure Driven Condensate Pump Trap Receiver Package

- Acceptable Manufacturers

  - Armstrong Intl, Inc. Model DPT-308 Low Boy™ Pump Trap Receiver Package

- Pump Trap body shall be constructed of carbon steel with all stainless steel internals. The mechanism shall incorporate Inconel X-750 springs for a long service life. Springs made of materials other than Inconel shall not be accepted. Single compression springs shall not be accepted.

- Pump Trap shall have a 3-Year No Fail Mechanism Warranty as standard.

- Motive Force. The Pump Trap shall utilize steam, compressed air or inert gas to remove condensate from the receiving vessel.

- Duplex pump package design with a maximum operating pressure of 125 psig.

- ASME code carbon steel receiver shall measure 12” x 48” or 24” x 48”, depending on the flash and condensate loads.  Packages have 0” fill head, 6” fill head, 12” fill head & 24” fill head designs available.

- Package shall be pre-piped between the pump inlet and receiver outlet as shown on drawings CDF1083 & CDF1084, and include isolation valves, bronze or stainless steel NPT check valves and unions.

- Pumps shall require no electricity for operation.

- The Pump Traps & Receiver shall include a bronze water level gauge with shut off valves.

- Provide Pump Traps with removable insulation covers.

- Provide Pump Traps with digital cycle counters.

- Manufacturer’s standard painting will apply.

Part 3 – Execution:

  - Installation

- Installation Compliance. Install in accordance with manufacturer’s instructions and as shown on the drawing.

- Insulation. Install the removable insulation cover in accordance with manufacturer’s instructions.

End of Section