HAFT-2448 Horizontal Flash Tank

Category: Horizontal Flash Tank

Model: HAFT-2448

Part 1	General

  - Summary

  - Submittals

  - Delivery, storage and handling

  - Warranty

Part 2	Products

  - Horizontal Flash Tank

Part 3	Execution

3.01 Installation

Part 1 – General

  - Summary

- Selection Includes

  - Armstrong HAFT-2448 Horizontal Flash Tank

  - Submittals

- Submit the following in accordance with this specification:

  - Tag number as referred to on drawing

  - Manufacturer’s name and model number

  - Capacity and Maximum Pressure Ratings

  - Materials of construction

  - Dimensions and weights

  - All other essential data as identified in Owner’s specifications.

  - Delivery, Storage and Handling

- Receipt. Contractor or end user shall receive and store flash tanks in a manner that will protect them from weather and construction activity.

- Examination. Upon receipt, contractor or end user shall visually inspect all flash tanks for damage and compare each tank to their corresponding specification.

  - Warranty. Product shall be free from defects in material and workmanship for a period of one (1) year from date of installation, but not longer than 15 months from date of shipment from the factory.  This warranty does not extend to any product that has been subject to misuse, neglect, or alteration after shipment from Armstrong factory.

Part 2 – Products

  - Horizontal Flash Tank

- Acceptable Manufacturers

  - Armstrong Intl, Inc. HAFT-2448 Horizontal Flash Tank

- The HAFT-2448 flash tank shall be a carbon steel ASME code Sec. VIII “U” stamped vessel rated for 150 psig maximum vessel pressure.

- ASME code carbon steel flash tank shall measure 24” x 48”.

- Flash tank shall have one (1) 1” NPT top side connections, one (1) 6” 150# flanged vent connection, one (1) 2” NPT top side inlet, one (1) 4” NPT side inlet, two (2) 3” NPT bottom outlets and one (1) 2” NPT bottom drain.

- Maximum condensate load and flash rate as shown on drawing CDF1099.

- Provide flash tank with removable insulation cover.

- Provide flash tank with gauge glass.

- Manufacturer’s standard painting will apply.

Part 3 – Execution:

  - Installation

- Installation Compliance. Install in accordance with manufacturer’s instructions and as shown on the drawing.

- Insulation. Install the removable insulation cover in accordance with manufacturer’s instructions.

End of Section