PT-104 Pump Trap

Category: Pump Trap

Model: PT-104

Part 1 – General

  - Summary

- Selection Includes

  - Pressure Driven Condensate Pump Trap

  - Submittals

- Submit the following in accordance with this specification:

  - Tag number as referred to on drawing

  - Manufacturer’s name and model number

  - Capacity and Maximum Pressure Ratings

  - Materials of construction

  - Dimensions and weights

  - All other essential data as identified in Owner’s specifications.

  - Delivery, Storage and Handling

- Receipt. Contractor or end user shall receive and store Pump Traps in a manner that will protect them from weather and construction activity.

- Examination. Upon receipt, contractor or end user shall visually inspect all condensate Pump Traps for damage and compare each pump to their corresponding specification.

  - Warranty. Guarantee that the equipment will be free from defects in materials and workmanship for a period of 36 months from date of installation but in no event longer than 39 months after shipment from Armstrong’s factory.

Part 2 – Products

  - Pressure Driven Condensate Pump Trap

- Acceptable Manufacturers

  - Armstrong Intl, Inc. Model PT-104 Pump Trap

- Body shall be constructed of Cast Iron with all stainless steel internals. The mechanism shall incorporate Inconel X-750 springs for a long service life. Springs made of materials other than Inconel shall not be accepted. Single compression springs shall not be accepted.

- Motive Force. The Pump Trap shall utilize steam, compressed air or inert gas to remove condensate from the receiving vessel.

- Pumps shall require no electricity for operation.

- The Pump Trap shall include a bronze water level gauge with shut off valves.

- Overall height of the pump shall not exceed 12-1/2””.

- Optional condensate inlet and outlet connections on the pump shall be provided for ease in piping.

- Check valves shall be either bronze or stainless steel.

- Provide Pump Trap with removable insulation cover and digital cycle counter.

- Manufacturer’s standard painting will apply.

Part 3 – Execution:

  - Installation

- Installation Compliance. Install in accordance with manufacturer’s instructions and as shown on the drawing.

- Insulation. Install the removable insulation cover in accordance with manufacturer’s instructions.