Mechanical PT-300 Series Packaged Condensate Removal System

Category: Condensate Recovery Equipment

Type: Mechanical

Model: PT-300 Series Packaged Condensate Removal System

General: Furnish steam/air operated mechanical condensate pumping system as specified herein.

Description:
The mechanical condensate pump trap package shall utilize steam or air as the motive force to remove condensate from the receiving vessel.  Electricity, seals, packings shall not be used.  The condensate pump trap package removal system shall be a complete pre-piped factory package consisting of, but not limited to, receiver tank, pump trap(s), and interconnecting piping, valves, and fittings.  The system shall be capable of removing ___________ pounds per hour condensate at ______ psig total back pressure.  System shall be Armstrong model PT- 3___ Series Packaged Condensate Removal System.

Pump traps shall be equal to Armstrong PT-3____ operated at _______psig steam (air).  Body vessel construction shall be carbon steel and ASME Section VIII “U” stamped.  Pump body vessel shall be horizontal design allowing a minimum of 12 gal  per cycle discharge and allow a maximum overall pump trap height of 21”.    Pump internals shall consist of an all stainless steel, float operated mechanism with actuating springs constructed of Inconel X-750 material.  Compression spring design shall not be acceptable.  Motive and vent valve/seats shall be externally replaceable without removing cap from the vessel body for cleaning and inspection.  

Liquid flow pipe connections shall be NPT.  Provide armored gauge glass to observe operation.  Each pump shall be equipped with inlet shut off valve; inlet check valve, unions, and outlet check valves.    Check valves shall be constructed of __________
material.   Discharge of each pump is to be independent (not piped to a common outlet) for separate field connections.  Provide custom design removable and reusable insulation jacket for optimum energy efficiency.  Each pump shall be equipped with a cycle counter to monitor the amount of condensate being returned.

Steel receiver tank shall be vented type, with a ______ gallon capacity.  Vent connection size shall be ____ inches, _______ connection type.  Inlet condensate connection shall be 
____inches , _____ connection type.  Provide armored gauge glass to observe operation.  Provide custom designed, removable and reusable tank receiver jacket.

Submittals and Testing:

The packaged condensate removal system shall be factory tested.  Stated pump capacities shall be tested and verified utilizing a minimum 200 F hot condensate and steam as the motive source.  Air as the motive source and cold water SHALL NOT be accepted.  Manufacturer shall supply verification of testing to ensure compliance.  The system manufacturer shall furnish complete installation and operation instructions.