PT-3508 Pump Trap

Category: Pump Trap

Model: PT-3508

Part 1 – General

  - Summary

- Selection Includes

  - Pressure Driven Condensate Pump Trap

  - Submittals

- Submit the following in accordance with this specification:

  - Tag number as referred to on drawing

  - Manufacturer’s name and model number

  - Capacity and Maximum Pressure Ratings

  - Materials of construction

  - Dimensions and weights

  - All other essential data as identified in Owner’s specifications.

  - Delivery, Storage and Handling

- Receipt. Contractor or end user shall receive and store Pump Traps in a manner that will protect them from weather and construction activity.

- Examination. Upon receipt, contractor or end user shall visually inspect all condensate Pump Traps for damage and compare each pump to their corresponding specification.

  - Warranty. Guarantee that the equipment will be free from defects in materials and workmanship for a period of 36 months from date of installation but in no event longer than 39 months after shipment from Armstrong’s factory.

Part 2 – Products

  - Pressure Driven Condensate Pump Trap

- Acceptable Manufacturers

  - Armstrong Intl, Inc. Model PT-3508 Pump Trap

- Body shall be constructed of Cast Iron with all stainless steel internals. The mechanism shall incorporate Inconel X-750 springs for a long service life. Springs made of materials other than Inconel shall not be accepted. Single compression springs shall not be accepted. Motive and vent connections shall have externally replaceable seats for viewing and inspecting the internal valves.

- Motive Force. The Pump Trap shall utilize steam, compressed air or inert gas to remove condensate from the receiving vessel.

- Pumps shall require no electricity for operation.

- The Pump Trap shall include a bronze water level gauge with shut off valves.

- Overall height of the pump shall not exceed 22”.

- Check valves shall be either bronze or stainless steel.

- Pump condensate inlet and outlet connections shall be 2” x 2” FNPT.

- Provide Pump Trap with removable insulation cover and digital cycle counter.

- Manufacturer’s standard painting will apply.

Part 3 – Execution:

  - Installation

- Installation Compliance. Install in accordance with manufacturer’s instructions and as shown on the drawing.

- Insulation. Install the removable insulation cover in accordance with manufacturer’s instructions.

End of Section