TPT-408 Low Boy™ Pump Trap Receiver Package

Category: Pump Trap

Type: Receiver Package

Model: TPT-408 Low Boy™

Part 1 – General

  - Summary

- Selection Includes

  - Pressure Driven Condensate Pump Trap Receiver Package

  - Submittals

- Submit the following in accordance with this specification:

  - Tag number as referred to on drawing

  - Manufacturer’s name and model number

  - Capacity and Maximum Pressure Ratings

  - Materials of construction

  - Dimensions and weights

  - All other essential data as identified in Owner’s specifications.

  - Delivery, Storage and Handling

- Receipt. Contractor or end user shall receive and store Pump Traps in a manner that will protect them from weather and construction activity.

- Examination. Upon receipt, contractor or end user shall visually inspect all condensate Pump Traps for damage and compare each pump to their corresponding specification.

  - Warranty. Guarantee that the equipment will be free from defects in materials and workmanship for a period of 18 months from date of purchase or one year from installation.

Part 2 – Products

  - Pressure Driven Condensate Pump Trap Receiver Package

- Acceptable Manufacturers

  - Armstrong Intl, Inc. Model TPT-408 Pump Trap Receiver Package

- Pump Trap body shall be constructed of carbon steel with all stainless steel internals. The mechanism shall incorporate Inconel X-750 springs for a long service life. Springs made of materials other than Inconel shall not be accepted. Single compression springs shall not be accepted.

- Pump Traps shall have a 3-Year No Fail Mechanism Warranty.

- Motive Force. The Pump Traps shall utilize steam, compressed air or inert gas to remove condensate from the receiving vessel.

- Triplex pump package design with a maximum operating pressure of 125 psig.

- Vented or ASME code carbon steel receiver and shall measure 24” x 72”. Connections shall include two 4” 150# RF flange, one 6” 150# RF flange, one 8” 150# RF flange and one 2” FNPT. The footprint of the package shall have an overall height of 70” with a skid measurement of 84” x 72”.

- Package shall be pre-piped between the pump inlets and receiver outlet as shown on drawing CDF1064 and include isolation valves, bronze or stainless steel NPT check valves and unions.

- Pumps shall require no electricity for operation.

- The Pump Traps and Receiver shall include a bronze water level gauge with shut off valves.

- Provide Pump Traps with removable insulation cover.

- Provide Pump Traps with digital cycle counters.

- Manufacturer’s standard painting will apply.

Part 3 – Execution:

  - Installation

- Installation Compliance. Install in accordance with manufacturer’s instructions and as shown on the drawing.

- Insulation. Install the removable insulation cover in accordance with manufacturer’s instructions.

End of Section